## Slide 1: Cells, Modules, & Arrays

## Slide 2: Types of PV Cells/Products
Single Crystal
Multi or Polycrystalline
Thin Film /Amorphous Silicon

## Slide 3: Monocrystalline Silicon
Warranties 25 years
Efficiency 12-21%
Notes: The main purpose of this and the subsequent slides is to show the students photos of the different technologies and how they appear when installed. Point out the physical characteristics (the dead white space in the mono panels for example).
The white box with the statistics is there to give the students a feel for the overall similarities and differences. Don’t spend too much time getting into the meanings of all the items, just relate them all to one another.

## Slide 5: Multi or Polycrystalline Silicon
Warranties 25 years
Efficiency 11-16%

## Slide 6
Multicrystalline ingot ready
for sawing
Cells ready for module assembly
Photos courtesy HomePower magazine/REC group

## Slide 7: Thin Film - used mainly for utility scale Amorphous Si (a-Si), CIGS, or CadTel
Warranties 20 -25 years
Efficiency 6-12%
Notes: It is good to point out that this is just one type of amorphous panel, this manufacturer, Unisolar, makes framed versions as well that are mounted like crystalline framed modules.

## Slide 8: Concentrating PV
Must Dual Axis-Track CPV

## Slide 9: PV Efficiencies (www.wikipedia.com)
1883 - less than 1% efficiency
1954 – AT&T labs marks 6% efficiency.
1955 - 2% efficient commercial solar cell for $25/cell or $1,785/Watt.
1957 - 8% efficient commercial solar cell
1958 - 9% efficient commercial solar cells
1959 - 10% efficient commercial solar cell
1960 - 14% efficient commercial solar cell
1976 - first amorphous silicon PV cells have an efficiency of 1.1%
1980 - thin-film solar cell exceeding 10% efficiency
1985 - 20% efficient silicon cell
1989 - Reflective solar concentrators are first used with solar cells.
1994 - concentrator cell (180 suns) becomes the first solar cell to exceed 30% conversion efficiency
2005 - Solar cells in modules convert around 17% of visible incidental radiant energy

## Slide 10: PV Materials & Efficiencies

## Slide 11: PV Modules
Many sizes and types available (5 – 435 watts)
Efficiencies 6 – 21%
Cells in series: 36 – 150
36 – 60 – 72 cells most common
25 year warranties
Currently ~$1/watt or less for most large modules bought in significant quantities

## Slide 15: PV Modules
Courtesy Home Power Magazine

## Slide 16: Silicon Cell Voltage
.5 - .6 volts/cell
Not related to size
Voltage affected by temperature
Open circuit voltage
Maximum power voltage
For Sharp 80 watt (36 cells)
Voc = 21.6/36 = .6 Voc/cell

## Slide 18: Silicon Cell Current Production
Related to size of cell
.2 amps/square inch or .03 amps (30 milliamps) per square centimeter
Affected by irradiance primarily
Short Circuit Current
  Used to determine maximum current
  Isc X 1.56 to estimate maximum current for wire sizing
Maximum Power Current

## Slide 19: Amperage is proportional to irradiance
If a module has a short-circuit current of 8 amps at 1000 w/m2, what would the short circuit current be at 623 watts/m2?
  623 watts/m2 ÷ 1000 watts/m2 = .623 or 62.3%
  8 A x .623 = 4.98 A

## Slide 20: Two factors that affect PV Module Performance
Temperature
Irradiance (solar power)

## Slide 21: Response to Temperature
Voltage
Current
T = 0 oC
T = 25 oC
T = 50 oC
Increasing temperature reduces voltage
Increasing temperature reduces power output
Increasing temperature increases current slightly
Decreasing temperature increases voltage
Notes: This is the first demonstration of how temperature affects voltage and current. The point of this slide is to show how voltage has a dramatic change with temperature while current change is minimal.
This is a good place to introduce the term “inversely proportional” in respect to temperature and voltage. We don’t need to get too far into specifics here, just show the general concept and how the IV curves move around.

## Slide 22: Response to Irradiance
Voltage
Current
1000 W/m2
750 W/m2
500 W/m2
250 W/m2
Current increases proportionally increasing irradiance
Voltage changes insignificantly with irradiance
Maximum power voltage changes little with irradiance
IV Curves at Constant Temperature
Notes: Another way to look at the effect of irradiance on current values. Since they got the concept in the last slide, this slide is intended to get them to evaluate how the IV curve is changed and even apply some math to determine the current values over varying irradiance values. Point out how the curves are shifting in the vertical dimension much more than the horizontal. You can even give a Isc value for a module at STC conditions and get them to calculate the new values for different irradiance values. This will come up again in the next slide so make sure they are aware of the way to accomplish it. Ask students to ID different points on the curves (Voc, Isc…)

## Slide 23: IV Curve

## Slide 24: Impact of Irradiance on Voltage & Current
Voltage increases rapidly, current increases proportionally w/ irradiance

## Slide 25: Series Wiring (Voltage Increases)

## Slide 26: Series Wiring

## Slide 27: Parallel Wiring (Amperage Increases)

## Slide 28: Series & Parallel

## Slide 31: Direct Grid Tie System

## Slide 32
48 Volt battery charging system

## Slide 33
        STC (Name Plate Rating)
        Cell temp 25 Degree C
        Irradiance 1000 W/square meter
        Air Mass Index 1.5
Standard Test Conditions (STC)

## Slide 34: Photovoltaic Device IV Curve at STC (25 C (77 F) and 1000 watts/m2)

## Slide 36: Calculating maximum voltage and maximum string size
  Example: How many modules, each having a Voc of 36.5 V can be placed in a series string without exceeding the 600 volt limit of a grid tie inverter when the record low temperature is -30 C?
Voc = 36.5 volts x 1.25 = 45.62 Voc
600 volt inverter/45.62= 13 modules

## Slide 37: Direct Grid Tie System

## Slide 39: Open Circuit Voltage Temperature Coefficient (% change per degree C)
Example
  How many Sharp 216 watt modules, each having a Voc of 36.5 V and temperature coefficient of -0.36%/C, can be placed in a series string without exceeding the 600 volt limit of a grid tie inverter when the record low temperature is -31 C?
    -0.36%/C = .36/100 = .0036
    .0036 x 36.5 V = .13 V/C
    Delta T = 25C to – 31 = 56 C
    .13 V/C x 56 = 7.28 volts
    36.5 Voc + 7.28 volts = 43.78 Voc @ -31C
    600 V/43.78= 13.7 modules = 13 modules max per string

## Slide 40: Choosing a module
Cost
Aesthetics
Material Warranty (years)
  Range of 1 – 10 years
Power Warranty (Years) – limited warranty for module power at STC minus power tolerance percentage (+/- 5%)
  20 years common at 90% for first 10 years and 80% for next 10 years (100 watts x .95 x .90 = 85.5 watts)
Power Density/Efficiency

## Slide 42
Module Namplate

## Slide 43: Module Specifications
Courtesy Home Power Magazine

## Slide 44: Quick Connects (MC, Tyco, etc)

## Slide 45
Field Serviceable Junction Box:
Less common today and found primarily on smaller modules
Sealed Junction Box:
Most common, safer to wire, but usually cannot replace leads
Courtesy Homepower Magazine/Kris SUtton
Module J-Box

## Slide 46: 1000 watts of crystalline PV fits in ~100 square feet.
How much space is needed?
Thin film efficiency is about half, so 500 watts of thin film in ~100 square feet

## Slide 47: How many modules do you need?
Each KW of PV array (4 – 250 watt modules) can produce about 1,000 KWH/year.
Average American House uses 10,000 KWH/year
10,000 KWH/year / 1000 KWH/KW = 10 KW
10 KW = 10,000 Watts/250 watts = 40 modules