## Slide 1: Inverters

## Slide 2: Inverter Functions
Change DC to AC
Increases or decreases voltage from array voltage to:
  120 Volts
  240 Volts
  208 Volts
Regulate Frequency
  50 HZ
  60 HZ
Feed Electricity back to grid
Battery Charging

## Slide 4: Input Ranges

## Slide 5: Inverter Wave Forms
Square wave
Modified Square Wave
Sine Wave

## Slide 6: Types
Stand Alone Inverters
  Battery based
Direct Utility Intertie
  No Battery
MultiFunction
  Battery charging grid tie

## Slide 7: Stand Alone Inverters

## Slide 8: Stand Alone

## Slide 9: Stand Alone Inverters
Considerations
  Maximum load
  Maximum surge
  AC output voltage
  Input battery voltage
100 watts to 60 KW
Pure sine & modified sine wave available
High Surge

## Slide 10: Modified Square or Modified Sine Wave Stand Alone Inverters
Types
  Xantrex TR Series
  Samlex
Least expensive - $.29 - .66/watt
Some electronic devices may buzz
Clocks don’t run accurately
Can’t charge battery packs, run laser printers, copiers, light dimmers, variable speed tools, Silicon Controlled rectifiers
High Surge
High Efficiency

## Slide 11: Xantrex TR Series Inverters
12 & 24 DC Volt Input
120 volt AC
1500 – 3600 watts
Modified sine wave
Battery charging capability
$.39 - .58/watt

## Slide 12: Sine wave Stand Alone Inverters

## Slide 13: Magnum
Makes sine wave & modified sine output inverters
600 - 4400 watts
12 – 48 volt models
120 & 240 models
$.50 - $1.19/watt

## Slide 15: Over Current Protection

## Slide 16: Sizing Overcurrent Protection
Divide rated output by lowest voltage that inverter will operate at to get maximum AC amps
Divide maximum AC amps by inverter efficiency to get maximum DC amps
Multiply maximum DC amps by 1.25 to avoid exposing conductor or overcurrent protection to more than 80% of its rated ampacity

## Slide 18: Example of Conductor & Circuit Breaker Sizing
2500 watts / 21 V = 119 amps AC
119 AC amps / .93 = 128 amps DC
128 x 1.25 = 160 amps (for continuous duty)
Conductor must have ampacity of 160 amps or more.
Circuit Breaker must also have amp rating of at least 160 amps also, but less than or equal to the ampacity of conductor used

## Slide 21: Direct Grid Tie Inverters

## Slide 22: Direct Utility Tied Inverters

## Slide 23: Direct Grid Tie Inverter

## Slide 24: Direct Grid Tie

## Slide 25: Grid Tie PV System

## Slide 30: Balance of System: Grid Tie

## Slide 32: Sunny Boy Inverter

## Slide 33: Sunny Boy with DC Disconnect

## Slide 37: Enphase Microinverters
http://www.youtube.com/watch?v=Fzj2a-9M4qo
http://www.youtube.com/watch?v=RC3mNUhcx6o

## Slide 39: Dual Function Inverters

## Slide 40: Multi-Function Inverters

## Slide 41: With Batteries & Grid

## Slide 42: Xantrex XW Battery Based Inverter

## Slide 43
http://www.youtube.com/watch?v=I91mHLu1Guw

## Slide 44: Xantrex XW Battery Based Inverter

## Slide 45: Outback Multifunction

## Slide 46: Multi – Function Inverters

## Slide 49: Multi Function Inverters

## Slide 50: Accessories