## Slide 1: Power Systems/DC disconnects & Junction Boxes
Integration Hardware/E-Panels

## Slide 2
PV array
Combiner Box
Battery
Charge Controller
Inverter
DC Junction Box

## Slide 3: Functions
Overcurrent protection
Solar Charge Controller PV Disconnect
Solar Charge Controller Battery Disconnect
Shunt location for system monitoring
Junction for conductors
DC Load center
Mounting Location for Charge Controller
Lightning protection

## Slide 4: Ananda Power Center 1990

## Slide 5: Heliotrope Solpan 30

## Slide 6: Trace or Xantrex DC250

## Slide 7: OutBack Power Systems Flexware (PSDC) Integration Hardware

## Slide 8: MidNite Solar E-Panel

## Slide 10: Midnite Solar E-Panels

## Slide 11: Midnite Mini-DC Disconnect

## Slide 12: Magnum E - Panels

## Slide 13: Schneider (Xantrex) XW System

## Slide 14: Schneider Conext SW with Midnite

## Slide 15: Components

## Slide 16: Circuit Breakers
DC rated circuit breakers for source circuits & Inverter/battery
Ground-Fault Detection & Interruption System

## Slide 17: Breaker Sizing for Charge Controller Wiring
Amp rating for 2 breakers used on either side of charge controller must be greater than Isc x 1.56 of each series string entering combiner box x number of series strings
Amp rating must be less than ampacity of wire used

## Slide 18: Example breaker sizing for system with 2 - 24 series strings
5.15 amps x 1.56 x 2 = 16 amps
2 breakers must be larger than 12.8 amps
Less than ampacity of wire used

## Slide 19: Minimum Breaker size for Inverter Wiring
Maximum continuous AC output wattage / efficiency
Maximum DC wattage divided by cut-out voltage

## Slide 20: Breaker Size for Inverter
2500 AC watts/.92 = 2717 DC watts
2717 DC watts / 21 volts = 129 amps
Breaker should be larger than 129 amps and need a conductor with an ampacity greater than 129

## Slide 23: Tri Metric Meter

## Slide 24: GFP or GFDI (Ground Fault Detector Interrupter)