## finca data
Finca Hydro
Pipe | 1.5" | poly | 1.5" poly
pipe length | 360 | ft | gpm | loss/100' | power
static pressure | 50 | psi | 20 | 2.81 | 142
static head (minus 20') | 95.5 | ft | 22 | 3.36 | 153
max available flow | 30 | gpm | 24 | 3.96 | 163
allowable friction loss @ 25% head loss | 6.6319 | ft/100 ft pipe | 26 | 4.58 | 171
allowable friction loss @ 33% head loss | 8.7542 | ft/100 ft pipe | 28 | 5.25 | 179
|  |  | 30 | 5.96 | 185
flow through the pipe | 30 | gpm | 35 | 7.94 | 195
with a resulting friction loss rate of | 5.96 | ft/100 ft pipe | 40 | 10.2 | 196
net head | 74.044 | ft | 45 | 12.7 | 187
expected power @ 53% efficiency | 185.11 | W | 50 | 15.4 | 167
2" poly
system voltage | 12 |  | gpm | loss/100' | power
wire run | 30 | ft | 20 | 0.83 | 154
current | 15.4258 | amps | 22 | 1 | 169
desired wire loss | 2.5 | % | 24 | 1.17 | 183
VDI | 15.4258 |  | 26 | 1.36 | 196
Wire size | #4 | AWG copper | 28 | 1.56 | 209
|  |  | 30 | 1.77 | 223
hydro daily energy at 20gpm | 3408 | Wh | 35 | 2.35 | 254
hydro daily energy at 30gpm | 4440 | Wh | 40 | 3.02 | 282
|  |  | 45 | 3.75 | 308
he would like this much energy from hydro | 1400 | Wh | 50 | 4.55 | 330
(plenty of surplus with the 1.5' pipe)
1.5" to 2' power increase
|  |  | 20 |  | 7.792%
|  |  | 22 |  | 9.467%
|  |  | 24 |  | 10.93%
|  |  | 26 |  | 12.76%
|  |  | 28 |  | 14.35%
|  |  | 30 |  | 17.04%

## Pipe Losses
PIPE FRICTION LOSS - PVC Class 160 PSI Plastic Pipe | [11 empty] | PIPE FRICTION LOSS
Pressure Loss from Friction in Feet of Head per 100 Feet of Pipe | [11 empty] | Polyethylene SDR - Pressure Rated Pipe
Pressure Loss from Friction in Feet of Head per 100 Feet of Pipe
Flow US GPM | Pipe Diameter, Inches
| 1 | 1.25 | 1.5 | 2 | 2.5 | 3 | 4 | 5 | 6 | 8 | 10 | Flow US GPM
1 | 0.05 | 0.02 | [10 empty] | 0.5 | 0.75 | 1 | 1.25 | 1.5 | 2 | 2.5 | 3
2 | 0.14 | 0.05 | 0.02 | [8 empty] | 1 | 1.13 | 0.28 | 0.09 | 0.02
3 | 0.32 | 0.09 | 0.04 | [8 empty] | 2 | 4.05 | 1.04 | 0.32 | 0.09 | 0.04
4 | 0.53 | 0.16 | 0.09 | 0.02 | [7 empty] | 3 | 8.6 | 2.19 | 0.67 | 0.19 | 0.09 | 0.02
5 | 0.8 | 0.25 | 0.12 | 0.04 | [7 empty] | 4 | 14.6 | 3.73 | 1.15 | 0.3 | 0.14 | 0.05
6 | 1.13 | 0.35 | 0.18 | 0.07 | 0.02 | [6 empty] | 5 | 22.1 | 5.61 | 1.75 | 0.46 | 0.21 | 0.07
7 | 1.52 | 0.46 | 0.23 | 0.08 | 0.02 | [6 empty] | 6 | 31 | 7.89 | 2.44 | 0.65 | 0.3 | 0.09 | 0.05
8 | 1.93 | 0.58 | 0.3 | 0.1 | 0.04 | [6 empty] | 7 | 41.2 | 10.5 | 3.24 | 0.85 | 0.42 | 0.12 | 0.06
9 | 2.42 | 0.71 | 0.37 | 0.12 | 0.05 | [6 empty] | 8 | 53.1 | 13.4 | 4.14 | 1.08 | 0.51 | 0.16 | 0.07
10 | 2.92 | 0.87 | 0.46 | 0.16 | 0.07 | 0.02 | [5 empty] | 9 |  | 16.7 | 5.15 | 1.36 | 0.65 | 0.18 | 0.08
11 | 3.5 | 1.04 | 0.53 | 0.18 | 0.07 | 0.02 | [5 empty] | 10 |  | 20.3 | 6.28 | 1.66 | 0.78 | 0.23 | 0.09 | 0.02
12 | 4.09 | 1.22 | 0.64 | 0.2 | 0.09 | 0.02 | [5 empty] | 12 |  | 28.5 | 8.79 | 2.32 | 1.11 | 0.32 | 0.14 | 0.05
14 | 5.45 | 1.63 | 0.85 | 0.28 | 0.12 | 0.04 | [5 empty] | 14 |  | 37.9 | 11.7 | 3.1 | 1.45 | 0.44 | 0.18 | 0.07
16 | 7 | 2.09 | 1.08 | 0.37 | 0.14 | 0.04 | [5 empty] | 16 |  |  | 15 | 3.93 | 1.87 | 0.55 | 0.23 | 0.08
18 | 8.69 | 2.6 | 1.33 | 0.46 | 0.18 | 0.07 | [5 empty] | 18 |  |  | 18.6 | 4.9 | 2.32 | 0.69 | 0.3 | 0.09
20 | 10.6 | 3.15 | 1.63 | 0.55 | 0.21 | 0.09 | 0.02 |  |  |  |  | 20 |  |  | 22.6 | 5.96 | 2.81 | 0.83 | 0.35 | 0.12
22 | 12.6 | 3.77 | 1.96 | 0.67 | 0.25 | 0.09 | 0.02 |  |  |  |  | 22 |  |  | 27 | 7.11 | 3.36 | 1 | 0.42 | 0.37
24 | 14.8 | 4.42 | 2.32 | 0.78 | 0.3 | 0.12 | 0.04 |  |  |  |  | 24 |  |  | 31.7 | 8.35 | 3.96 | 1.17 | 0.49 | 0.16
26 | 17.2 | 5.13 | 2.65 | 0.9 | 0.35 | 0.14 | 0.05 |  |  |  |  | 26 |  |  | 36.8 | 9.68 | 4.58 | 1.36 | 0.58 | 0.21
28 | 19.7 | 5.89 | 3.04 | 1.04 | 0.41 | 0.16 | 0.05 |  |  |  |  | 28 |  |  |  | 11.1 | 5.25 | 1.56 | 0.67 | 0.23
30 | 22.4 | 6.7 | 3.45 | 1.17 | 0.43 | 0.18 | 0.05 |  |  |  |  | 30 |  |  |  | 12.6 | 5.96 | 1.77 | 0.74 | 0.25
35 |  | 8.9 | 4.64 | 1.56 | 0.62 | 0.23 | 0.07 |  |  |  |  | 35 |  |  |  | 16.8 | 7.94 | 2.35 | 1 | 0.35
40 |  | 11.4 | 5.89 | 1.98 | 0.78 | 0.3 | 0.09 | 0.02 |  |  |  | 40 |  |  |  | 21.5 | 10.2 | 3.02 | 1.27 | 0.44
45 |  | 14.2 | 7.34 | 2.48 | 0.97 | 0.37 | 0.12 | 0.04 |  |  |  | 45 |  |  |  | 26.8 | 12.7 | 3.75 | 1.59 | 0.55
50 |  | 17.2 | 8.92 | 3.01 | 1.2 | 0.46 | 0.14 | 0.04 |  |  |  | 50 |  |  |  | 32.5 | 15.4 | 4.55 | 1.91 | 0.67
55 |  | 20.5 | 10.6 | 3.59 | 1.43 | 0.55 | 0.16 | 0.05 |  |  |  | 55 |  |  |  |  | 18.3 | 5.43 | 1.96 | 0.81
60 |  | 24.1 | 12.5 | 4.21 | 1.66 | 0.64 | 0.18 | 0.07 | 0.02 |  |  | 60 |  |  |  |  | 21.5 | 6.4 | 2.7 | 0.94
70 |  |  | 16.6 | 5.61 | 2.21 | 0.85 | 0.25 | 0.09 | 0.03 |  |  | 65 |  |  |  |  | 23.8 | 7.41 | 3.13 | 1.08
80 |  |  | 21.3 | 7.18 | 2.83 | 1.08 | 0.32 | 0.12 | 0.04 |  |  | 70 |  |  |  |  | 28.7 | 8.49 | 3.59 | 1.24
90 |  |  |  | 8.92 | 3.52 | 1.36 | 0.39 | 0.14 | 0.07 |  |  | 75 |  |  |  |  | 32.6 | 9.67 | 4.07 | 1.4
100 |  |  |  | 10.9 | 4.28 | 1.66 | 0.48 | 0.18 | 0.07 | 0.02 |  | 80 | [5 empty] | 10.9 | 4.58 | 1.59
150 |  |  |  | 23.2 | 9.06 | 3.5 | 1.04 | 0.37 | 0.16 | 0.05 |  | 85 | [5 empty] | 12.2 | 5.13 | 1.77
200 |  |  |  |  | 15.5 | 5.96 | 1.75 | 0.62 | 0.28 | 0.07 | 0.02 | 90 | [5 empty] | 13.5 | 5.71 | 1.98
250 |  |  |  |  | 23.4 | 9.05 | 2.65 | 0.94 | 0.42 | 0.12 | 0.05 | 95 | [5 empty] | 15 | 6.31 | 2.19
300 | [5 empty] | 12.6 | 3.73 | 1.34 | 0.58 | 0.16 | 0.05 | 100 | [5 empty] | 16.5 | 6.92 | 2.42
350 | [5 empty] | 16.8 | 4.95 | 1.78 | 0.76 | 0.21 | 0.07 | 150 | [5 empty] | 34.5 | 14.7 | 5.11
400 | [5 empty] | 21.5 | 6.33 | 2.25 | 0.97 | 0.28 | 0.1 | 200 | [6 empty] | 25 | 8.7
450 | [6 empty] | 7.87 | 2.81 | 1.2 | 0.32 | 0.12 | 300 | [7 empty] | 18.4
500 | [6 empty] | 9.55 | 3.41 | 1.45 | 0.42 | 0.14
550 | [6 empty] | 11.4 | 4.07 | 1.75 | 0.48 | 0.16
600 | [6 empty] | 13.4 | 4.78 | 2.05 | 0.58 | 0.18
650 | [6 empty] | 15.5 | 5.54 | 2.37 | 0.67 | 0.23
700 | [6 empty] | 17.8 | 6.37 | 2.71 | 0.76 | 0.25
750 | [6 empty] | 20.3 | 7.22 | 3.1 | 0.86 | 0.3
800 | [7 empty] | 8.14 | 3.5 | 0.97 | 0.32
850 | [7 empty] | 9.11 | 3.89 | 1.08 | 0.37
900 | [7 empty] | 10.1 | 4.32 | 1.2 | 0.42
950 | [7 empty] | 10.8 | 4.79 | 1.34 | 0.46
1000 | [7 empty] | 12.3 | 5.27 | 1.45 | 0.51

## vdi
FEET IS ONE WAY DISTANCE
VOLT DROP IS WHOLE NUMBER (IE. 2% = 2)