## Slide 1: Combiner Boxes & Disconnects
PV combiner boxes are commonly used to parallel either multiple PV modules or series strings of modules and provide series overcurrent protection as specified by the National Electrical Code (NEC)

## Slide 2: Functions of Combiner Boxes
Overcurrent protection for modules & conductors
Bonding location for conductors designed to avoid voltage drop and conductors sized for ampacity
Combines series strings in parallel
Allows one to remove a module, subarray or series string from array without affecting the rest of the array
Can be a location to disconnect DC power from Inverter
Grounding terminal location
Lighting arrestor location

## Slide 3
Daisy Chain
vs
Combiner Box Wiring

## Slide 7: Direct Grid Tie System

## Slide 8: Midnight Solar PV Combiner

## Slide 9
Outback Combiner Box

## Slide 11: Outback Combiner Boxes

## Slide 12: Disconnecting Combiner Boxes

## Slide 13: Fuses & Fuse Holders
DO NOT open under load

## Slide 14
Integrated Disconnect
Fused Combiner
Inverter Integrated Combiner

## Slide 15
SolarBOS Integrated Disconnect
Fused Combiner
Large Commercial or Utility Scale Combiner Box

## Slide 16
Integrated Disconnect
Fused Combiner
Large Commercial or Utility Scale Combiner Box

## Slide 17
Integrated Disconnect
Fused Combiner
Large Commercial or Utility Scale Combiner Box - Contacting Combiner

## Slide 18: Roof Mounted Combiners

## Slide 19: Overcurrent Devices
Fuses & Circuit Breakers
  All overcurrent devices designed to open the circuit when subjected to current exceeding their nominal rating
  Ungrounded conductors in all circuits are required to have overcurrent protection
  Must be DC rated and have adequate DC voltage rating
  Disconnect mechanism is required

## Slide 20: Fuses & Fuse Holders
Need to consider amperage rating and voltage rating

## Slide 21: Circuit Breakers

## Slide 22
http://www.midnitesolar.com/video/spd/spd.php
Midnite Surge Protection Device $119.00

## Slide 23: Surge Protection

## Slide 24: Over Current Device Requirements for Combiner Boxes
Fuse or circuit breaker size must be less than the series fuse rating of module or the temperature derated ampacity of the conductor, whichever is less
Fuse or circuit breaker must be greater than the Isc x 1.56
Fuse or circuit breaker should be DC rated
Fuse or circuit breaker must have a voltage rating higher than the Voc at record low temperature
Fuse or circuit breaker should be UL listed
Fuse needs to be in “touch-safe” holder

## Slide 26
DC Voltage rating of all wiring disconnects &
over current devices must be 25% over Voc of PV array or use correction factor from NEC Table 690-7 when lowest ambient temperature is known or calculate using the Voc temperature coefficient of PV modules being used

## Slide 27: Example Voltage Estimation
If 8 - 24 volt modules are connected in series for a direct grid tie system, what should be the voltage used to select overcurrent devices if lowest expected temperature is -30 F. (Voc temperature coefficient is -.36%/C)
(Voc/module @ 25 C = 44.4 volts)
  8 modules x 44.4 Voc x 1.25 = 444 volts
        or
  -.36%/c = .36 / 100 =.oo36 x 44.4 Voc = .1598 Volts / C
  .1598 x (-30 – 25) = .1598 x 55 = 8.79 volt increase over 25 C (STC)
  (44.4 + 8.79) x 8 = 425 volts

## Slide 29: Overcurrent Device Sizing Example
What size fuse or circuit breaker should I use in a combiner box when 4 – Sharp 80 watt 12 volt (36 cell) PV modules are wired in series to make a 48 volt series string. The Isc is 5.15 amps. So 5.15 x 1.56 = 8 amps. The modules have a series fuse rating of 10 amps. Module Voc is 21.6 and record cold temperature is -31 and temperature Coefficient of Voc = -.36%/C
    Over current rating needs to be less than or equal to the series fuse rating of module which is 10 amps
    Overcurrent device needs to be greater than or equal to 8 amps
    So use a 8 - 10 amp DC rated fuse or circuit breaker
    Voltage rating for over current device =
    .0036 x 21.6 = .077 Volts/C
    .077 V X (-31 – 25) = 4.35 Volt increase at -31
    Voc = 21.6 + 4.35 = 25.95 @ -31 C
    Array Voc = 25.95 x 4 = 103.8 Voc

## Slide 30: Disconnects
Equipment – from all power sources
PV Power Source - DC Disconnect
PV System – AC Disconnect
Current and voltage ratings must be adequate
Courtesy Don Hursey

## Slide 31: DC Disconnects
Usually bigger and more expensive than AC disconnects
Check voltage and current ratings for all disconnects to make sure they meet or exceed circuit requirements
Courtesy Don Hursey

## Slide 32: AC & DC Disconnect in Grid Tied System

## Slide 33: 12 Volt P V Array

## Slide 34: Connecting to Mounting pole
Uni-strut: 5/8” deep and 1 5/8” deep

## Slide 35: Combiner Box Circuit Breakers

## Slide 36: 2 Parallel Strings in Combiner Box

## Slide 37: Lightning Arrestor & Grounding Electrode Conductor

## Slide 38: Lightning Arrestor, Equipment Ground, & Grounding Electrode Conductor

## Slide 39: Equipment Grounding

## Slide 40: Combiner Box

## Slide 41: Combiner Box Completed

## Slide 42: Pole Mounted Combiner Box

## Slide 43: Pole Mounted Combiner Box