## PV System Sizer
PV System Sizing Program for 36 or 72 cell modules with PWM Controller
Load Analysis
AC Loads
AC Device | Device Watts | Hours of daily use | Days of use per week | Average watt-hour per day
LED Lighting (6 Lights) | 54 | 4 | 7 | 216
SunFrost Refridge | 48 | 8 | 7 | 384
Water Pumping | 50 | 6 | 7 | 300
Satellite TV | 60 | 5 | 7 | 300
Telephone | 6 | 24 | 7 | 144
Espresso Maker | 1350 | 0.1 | 7 | 135
Computer | 45 | 6 | 7 | 270
0
0
0
0
0
0
0
0
0
0
0
0
| Total AC watt-hrs/ day: |  |  | 1749
| AC to DC watt-hrs/day: |  |  | 1943.3333
(divide by inverter efficiency of 90% or .90)
DC Loads
DC Device | Device Watts | Hours of daily use | Days of use per week | Average watt-hour per day
0
0
0
0
0
0
0
| Total DC watt-hours/ day |  |  | 0
Array Sizing
Total DC watt-hours/ day |  |  | 1943.3333
System Nominal Voltage (12, 24, 48) |  |  | 24
Total DC amp-hours/ day |  |  | 80.9722
Total daily amp-hour requirement |  |  | 97.1667
(corrected for battery/ wiring losses, safety factor) |  |  | xxxxxxxx
Estimated insolation |  |  | 4.5
(hours of full sun per day or KWH/m2/day) |  |  | xxxxxxxx
Total PV array currrent (amps) |  |  | 21.5926
Selected PV module nominal voltage |  |  | 12
Selected PV module rated power (amps) |  |  | 5.03
Number of Series Strings required in parrallel |  |  | 5
Number modules required in series |  |  | 2
Total modules required |  |  | 10
Battery Sizing
Reserve time desired (days) |  |  | 5
Fraction of useable battery capacity (50%-80%) |  |  | 75%
Minimum battery capacity (in amp-hours) |  |  | 647.7778
Selected battery amp-hour capacity |  |  | 225
Number of series strings required in parrallel |  |  | 3
Selected battery voltage (usually 6 or 12) |  |  | 6
Number of batteries required in series |  |  | 4
Total number of batteries required |  |  | 12
Total modules required |  |  | 10
Total number of batteries required |  |  | 12