## Sheet1
F-Chart Method
Duffie and Beckman, along with Goswami
Did regression analysis and came up with a way to predict solar
performance using two variables, X and Y
f-Chars developed for three system configurations:
1. Space and water heating with water as the fluid
2. Space and water heating with air as the working fluid
3. process hot water
Figure 7.14 as basic system configuration for type 1 above:
Solar collector(s)
3 heat exchangers
Main storage tank
Pre heat tank
Auxilary space and water heating
The space and water heating loads
X = [AcF'RUL * Dt * (100-Ta)] / L
F'R = 0.97 * FR
Ta = monthly average temperature
Dt = number of hours in the month
so,
X = [Ac*0.97*FRUL * Dt * (100-Ta)] / L
Y = [Ac*0.97*FRUL * ta * HT*N]/L
HT = Monthly average daily radiation on collector
N = number of days in the month
ta = | Monthly average product for the collector = 0.96 * ta
f = 1.029 * Y - 0.065 * X - 0.245 * Y^2 + 0.0018 * X^2 + 0.0215 * Y^3
Figure 7.15
Example 7.3
| days | daily I | Load | Avg T
jan | 31 | 3.8 | 140 | 7.2
feb | 28 | 4.5 | 120 | 9.4
mar | 31 | 4.9 | 80 | 13.7
apr | 30 | 5.2 | 50 | 17.8
may | 31 | 5 | 28 | 21.8
jun | 30 | 4.9 | 20 | 25.6
jul | 31 | 4.8 | 20 | 27.2
aug | 31 | 5 | 20 | 27
sep | 30 | 5 | 20 | 24.1
oct | 31 | 5.2 | 40 | 17.8
nov | 30 | 4.3 | 80 | 13.1
dec | 31 | 3.8 | 110 | 9.1
N