## Slide 1
Microhydro System Design & Installation
Course Number: AECAIA092614 A
Michael Uchal
Date: September 26-27, 2014
Appalachian State University
Provider Number: 60114136

## Slide 2
10 LU Credits earned on completion of this course will be reported to AIA CES for AIA members. Certificates of Completion for both AIA members and non-AIA members will be received at the end of the class.
Engineers will self report with their Certificate of Completion.
This course is registered with AIA CES for continuing professional education. As such, it does not include content that may be deemed or construed to be an approval or endorsement by the AIA of any material of construction or any method or manner of handling, using, distributing, or dealing in any material or product.
_______________________________________
Questions related to specific materials, methods, and services will be addressed at the conclusion of this presentation.

## Slide 3
Course
Description
This 1-1/2 day workshop will cover the basics of small scale hydro power with a field trip to local microhydro installation. Participants will learn about: site assessment techniques including the measurement of head and flow; system design; types of turbines and their associated performance and cost; system components such as the intake, penstock and balance of system; maintenance and troubleshooting; and case studies. Please join us for 1-1/2 days packed with information and site visits for hands on demonstrations.

## Slide 4
Learning
Objectives
1. Participants will learn about the basics of small scale hydro power.
2. Participants will learn about site assessment techniques including the measurement of head and flow, system design, and types of turbines.
3. Participants will learn costs associated with the performance a microhydro system, system components and maintenance.
4. Participants will visit a local microhydro installation, learn about maintenance, troubleshooting, and case studies.
At the end of the this course, participants will be able to:

## Slide 5: Tentative Agenda
Friday, September 18, 2015
9:00 Hydro Presentation in Classroom
12:00 Lunch at ASU
1:00 Travel to Mollies Branch Hydro Site
3:00 Hydro Presentation in Classroom
Saturday, September 29, 2015
9:00 Hydro Presentation in Classroom
1:00 Conclude for the day

## Slide 6: Introductions
Who are you? What are you interested in?

## Slide 7: Hydro Power
Renewable energy in water that flows from a higher to a lower elevation under the influence of earth’s gravitational field
Yosemite National Park

## Slide 8: Hydro, Driven by Solar Power

## Slide 9
Existing hydroelectric plants (yellow) and potential high head/low power energy sites (orange) in the conterminous United States. Purple represents areas excluded from hydropower development due to Federal statutes and policies. Source: Water Energy Resources of the United States with Emphasis on Low Head/Low Power Resources (p. 47), U.S. Department of Energy

## Slide 10: Hydro Stats

## Slide 12: Hydropower Categories
Nano <100 W
Pico <5 kW
Micro <100 kW
Mini <1000 kW
Small <10 MW
Large 10MW and UP

## Slide 13
Most of that global hydro power is produced by small and large-scale hydroelectric plants

## Slide 14
Hills Creek Dam (Type: Storage) Willamette River, Oregon Corps of Engineers In service: May 2, 1962 30 MW

## Slide 15
wikimedia.org
Bonneville Dam
(Type: Run-of-river) Columbia River
Oregon/Washington border >1,000 MW

## Slide 16: Largest: Three Gorges Dam
Proposed 22,500 MW (~2011)

## Slide 17
We don’t need a river, just some falling water to tap into

## Slide 18
We don’t need a river, just some falling water to tap into

## Slide 19: What is Microhydro?
With the right resource, microhydro systems enable clean, renewable, on-site generation of electricity at an affordable price with minimal environmental impact.
Defined as electricity generated from falling water with a capacity less then 100 kW.

## Slide 20: Why Microhydro?
Affordable (often the most affordable)
Reliable
No air pollution
No waste products
Can be a good resource in the mountains
Microhydro is often the most cost effective way to renewably generating electricity - in many cases competing with the price of grid power - with no emissions.

## Slide 21: Hydro Potential in Western NC
1592 potential sites with 5 – 200 KW potential in 24 western counties
Many more with less than 5 KW
  1KW site would be adequate to power a conventional home
28 MW total output capacity
308 million kWh annual output (30,000 houses)

## Slide 22: Regulations
The US Army Corps of Engineers has jurisdiction over virtually all waterways in the United States.
  If you plan on moving a rock in a stream you better ask first!

## Slide 23: Mechanical Power from Water Wheels began 2000 years ago

## Slide 24: Microhydro Power Today

## Slide 25
These Turbines are turned by water. That turning motion transfers energy by causing coils of wire to move relative to magnets.
With the high head situations we commonly see in the mountains, pelton wheels and turgo wheels are commonly used.
Jets are sprayed into cups of these wheels

## Slide 26
At the heart of the micro hydro system is a water wheel or turbine enclosed within a structure.
 | high head | medium head | low head
impulse turbines | Pelton Turgo | cross-flow multi-jet Pelton Turgo | cross-flow
reaction turbines |  | Francis Pump-as-turbine (PAT) | propeller Kaplan

## Slide 27
High Head, Low Flow Low Head, High Flow
https://www.google.com/search?q=hydro&client=firefox-a&hs=hp6&rls=org.mozilla:en-US:official&channel=sb&source=lnms&tbm=isch&sa=X&ei=NDggVNSWNeLGsQS5_4KgAg&ved=0CAgQ_AUoAQ&biw=1682&bih=920#rls=org.mozilla:en-US:official&channel=sb&tbm=isch&q=hydro+turbine&facrc=_&imgdii=_&imgrc=LyX_HmLqt1AEgM%253A%3BWqrtR5w7-6nRfM%3Bhttp%253A%252F%252Fwww.raine-or-shine.com%252Fimages%252Fhydro-diag.png%3Bhttp%253A%252F%252Fwww.raine-or-shine.com%252Fwind-water-turbines.php%3B390%3B292

## Slide 28: System Basics

## Slide 29: System Components
Intake
Penstock or pipe
Turbine / power house
Tailrace
Balance of System
  Controller
  Battery bank
  Disconnect
  Dump load
  meter

## Slide 30
The Hydro Resource

## Slide 31: Why is resource assessment important?
It wont work without the resource! (Lawn ornament)
It will not provide a return on investment without working!
You MUST have both HEAD and FLOW for a successful hydro system!!!!!!!!!

## Slide 32: Hydro Power Output
Power output (watts) = Flow (GPM) X Net Head (ft)
8 – 12

## Slide 33: Measuring Head
https://www.transitionnetwork.org/news/2012-07-19/measuring-transition-important-survey

## Slide 34: Static Head vs. Dynamic / Net Head
Static Head
Dynamic Head
The amount of head when the water is not moving.
Does not account for the friction of the pipe as water flows down the penstock
Amount of head when water is flowing through the penstock
Is always lower than static head due to friction losses.
You want to minimize this loss.
Stay tuned on how to achieve this

## Slide 35: Measuring Static Head
Stick with carpenters level
Sight level
Water level
Pipe with pressure gauge
GPS Unit
Transit
Topo map
Altimeter
While you are on site, you could measure the penstock length as well.

## Slide 36: Measuring Static Head
5’ stick with level (3 people)
5’

## Slide 37: Measuring Static Head
Sight level (2 people)
Eye level

## Slide 38
Remember, you don’t have to follow the creek.
Make sure your elevations are the same as the actual site, or correct for differences.

## Slide 39: Measuring Static Head
Water level and measuring tape
(2 people)
(Good for low head)
Water level
Hose filled with H2O

## Slide 40: Measuring Static Head
Transit
Most accurate if you have the equipment

## Slide 41: Measuring Static Head
Pipe with pressure gauge at the bottom
Could use garden hose(s)
2.31 feet = 1 psi
Or 0.43 psi / foot
This gauge reads 38 psi
38 psi x 2.31 feet/psi = 88 ft of static head

## Slide 42: Measuring Static Head
GPS, altimeter, topo map, google earth.
Difference in elevation readings
Not accurate enough for most system calculations and design
  Often used as a preliminary assessment.
  Save time and fuel!

## Slide 43: Measuring Flow

## Slide 44: Measuring Flow
Units
  GPM: gallons per minute
  CFM: cubic feet per minute
  CFS: cubic feet per second
How much to use?
  Don’t take the whole creek!
  Use minimum flow
  Avoid taking more than ½ of the flow max
      (1/3 is preferred)
  Let the ecosystem thrive

## Slide 45: Methods of Flow Assessment
Container method
  Small stream, small waterfall
Float method
  Larger, flat, uniform stream
V-notch Weir
Rectangular Weir
Make several measurements to assess seasonal variation
More difficult method:
Used for long term studies

## Slide 46: Container Method: high head low flow
This may be tricky, but possible!
Small stream, little waterfall

## Slide 47: 5 gallon bucket - only good up to 300gpm

## Slide 48: 5 gallon bucket
If the measured flow using a 5 gallon bucket and a stop watch was 5 gallons in 1.5 seconds, how many GPM would this be?

## Slide 49: 5 gallon bucket
If the measured flow using a 5 gallon bucket and a stop watch was 5 gallons in 1.5 seconds, how many GPM would this be?

## Slide 50: Float method
Big, flat, uniform creek

## Slide 52: Float method
Calculate the average depth
Lay a straight edge across the stream, measure the depth every foot, average the depths

## Slide 53: Float method
2. Calculate the cross sectional area
Area (ft2) = Average depth (ft) x Width (ft)

## Slide 54: Float method
3. Calculate velocity
Measure where you measured the area, an orange makes a good float, start well upstream, a 10’ span is good, average multiple measurements.

## Slide 55: Float method
5. Correct for Friction
Flow (ft3/s) = Velocity (ft/s) x Cross Sectional Area (ft2) x .83
Multiply x 0.83 to correct for friction on the bottom of the stream

## Slide 56: Float Method
So, if these guys measure this 3’ wide stream and get an average depth of 8” and it takes an orange an average 5 seconds to go 10 feet, what is the flow in GPM?
Area = 3’ x 8” x (1’/12”) = 2 ft2
Velocity = 10 ft/5 s = 2 ft/s
Flow = 2 ft2 x 2 ft/ s = 4 ft3/s
4 ft3/s x 7.48 gal/1 ft3 x 60s/1 min = 1795 gpm
Correct for friction, 1795 gpm x .83 = 1490 gpm

## Slide 57: Weir Method
For larger flows or more accurate measurements over time
Small
  V-notch
Larger
  Rectangular
All you needs is depth and the table

## Slide 58: Needed info: Weir Width

## Slide 59: Needed info: Water depth

## Slide 60: Reference Chart: use chart to determine flow
Assume the following:
Your weir opening is 15 inches wide
The water depth is 7.25 inches deep
What is your flow in cfm?
Answer: for 7-1/4 inch deep water 7.80 cfm move through the weir opening / inch.
Multiply this number by the width of your weir opening. In this case 15 inches.
117 cfm or 875 gpm

## Slide 61: V-notch Weir

## Slide 62
System Design
http://www.ericsson.com/uxblog/2012/09/automagic-some-user-experience-design-principles/

## Slide 63: Basic Components of the System
H2o Intake
Pipeline/penstock
Turbine
Balance of system
Tailrace

## Slide 64: Intake Design
Supply water to the system
Intake must:
  Screen out rock and other debris ¼-inch and larger
    (High head systems– remove silt as well)
  Keep out water creatures – fish and others aquatic life
  Reduce the formation of air bubbles entering the system
Ouch!!!!!!

## Slide 65: Pipe with a screen
Benefits:
  Simple construction
  Low cost
Drawbacks:
  Must be cleaned often
Home Power Magazine

## Slide 66: Open Pipe with Settling Container
Benefits:
  Low maintenance
  Low cost
  Filter find particulates
Drawback:
  Can cause air bubbles
Home Power Magazine

## Slide 67: Screen Box
Benefits:
  Catch a lot of debris
Drawback:
  Difficult to construct
  Hard to clean
  Requires a weir
Home Power Magazine

## Slide 68: Pond Bucket
Benefits:
  Ease of construction
  Low air intake
Drawbacks:
  Requires slow moving
  Water
  Difficult access for
  cleaning
Home Power Magazine

## Slide 69
Culvert Intake / Tap
Benefits:
  Uses existing infrastructure
Drawbacks
  Difficult to construct
  Restricts culvert flow
Spillway – Coanda Effect
Benefits:
  Self-cleaning
  Recued ecological impact
Drawback:
  Expensive
Home Power Magazine

## Slide 70: The Intake Diverting clean water into the penstock
Hydro-Shear Coanda Effect screen
Start of Penstock
Steam Flow
Shown here:
www.hydroscreen.com

## Slide 71
Slow-Water Water Diversion
Benefits:
  Large Streams
Drawbacks:
  Construction difficulty
  Stream blowout
Siphon Intake
Benefits:
  Easy installation
Drawbacks:
  Needs screen
  Losses prime
  Special priming process
Home Power Magazine

## Slide 72: The Intake Diverting clean water into the penstock
Screen
Start of Penstock
Steam Flow
A sandy/silty creek may need more settling time
Overflow

## Slide 73: Pipeline / Penstock
The component that delivers the water to the turbine.

## Slide 74: Factors to Consider
surface roughness
design pressure
method of jointing
weight and ease of installation
accessibility of the site
terrain
soil type
design life and maintenance
weather conditions
availability
relative cost
likelihood of structural damage.

## Slide 75: Burying Pipe
Burying the penstock improve aesthetics.
It is vital to ensure a buried penstock is properly and meticulously installed
  subsequent problems such as leaks are much harder to detect and rectify.
A good idea if using PVC

## Slide 76: Penstock Support System PVC likes to stay straight HDPE can follow the contour of the ground

## Slide 77: Penstock Materials
Steel
  Rust, rough (high losses)
  High wear and high pressure (road crossing, bottom of penstock)
AL irrigation pipe
  Low pressure rating
  Can’t be buried or else it will corrode
Pressure Rated PVC
  Readily available and easily joined
  UV degradation and physical damage
  Buried, covered or painted
PVC sewer pipe
  Low-budget, not pressure-rated!
HPDE (Polyethylene)
  Toughest, you can drag it into place, can be exposed to sunlight
  Joined by a fusion welder

## Slide 78: Fusion Welding

## Slide 79: Pipe Friction Losses
Must use charts to calculate head loss due to pipe friction
Flow varies with D3
  4” pipe can flow 8x more water than 2” pipe

## Slide 80: Designed System Flow and Output
Designed Flow = Amount of Flow you will use from a hydrological system.
The sites flow can fluctuate during the year!
You can design around these constraints:
You have Options!
Option #1
  Determine the low or most constant flow and design a system around this flow.
Option #2
  Determine high and low median flows and design a system that can adapt to these conditions.
    This may take more site assessment throughout the year and ultimately cost more, but could save more in the end.
More on how to do this a little later!

## Slide 81: Choosing your Penstock
Factors to determine:
  Volume of Water
  Material
  Diameter of Pipe
  Length of Pipe
  Changes in Direction

## Slide 82: Other Penstock Design Considerations
Reduce Air
Reduce Turbulence by:
  Keep penstocks as straight as possible!
  Steady elevation declines
Standpipe Vent

## Slide 83: Steady elevation declines
Keep the declines as consistent as possible.
If you form high spots, include a bleeder valve.
Home Power 125

## Slide 84: Keep them straight and constant (as possible)
Both the penstock and the manifold!

## Slide 85: Avoid sudden enlargements!

## Slide 86: Solution: Gradual Enlargements!
7 degree angle of enlargement is optimal for most fittings!

## Slide 87: Avoid sudden constrictions!

## Slide 88: Solution: Gradual Constrictions!
Source: westerndynamics. Com for all pipe images.

## Slide 89: Step 1: After you have determine static head, flow, and penstock length
Determine allowable penstock losses:
  System losses should be between 5% and 20%
    This is for financial reasons. Larger pipe costs more and is often not worth the investment for small efficiency gains.
  Remember: larger pipe has less friction loss!
    All determined based on cost of pipe and achievable outputs
      Larger diameter pipe costs more – you may want a lower efficiency to save on installation cost.

## Slide 90: Step 2: Determine a high and low friction loss
Assume the following:
140 ft static head
300 GPM max stream flow
200 GPM min stream flow
Design flow of 100 GPM?
1300’ penstock
What size PVC pipe will be best?

## Slide 91: Step 2: Determine a high and low friction loss
Efficiency loss of 5% (low loss):
Total Static Head: 140 feet
  140 feet X .05 = 7 feet
  140 static head – 7 feet of total loss = 133 feet dynamic head
Efficiency loss of 20% (high loss):
Total Static Head: 140 feet
140 feet X .20 = 28 feet
140 static head – 28 feet of loss = 112 feet of dynamic head

## Slide 92: Step 3: Determine Pipe Diameter
    1. Use the Penstock chart to determine friction losses / 100 feet of pipe.
    2. Look-up your designed flow on
    the left column
    3. Compare it to different diameter
    pipes.
    4. Convert PSI to feet (if necessary)
    PSI X 2.31 = feet of head
    5. Multiply by # of 100 foot lengths

## Slide 93: Step 3 Cont.: Determine Pipe Diameter
    1. Use the Penstock chart to determine friction losses / 100 feet of pipe.
    2. Look-up your designed flow on
    the left column (100 GPM)
    3. Total loss is 6.29 (2 in.) 0.92 (3 in.)
    4. Convert 0.92 psi to feet
    0.92 X 2.31 = 2.12 feet
    5. Multiply by # of 100 foot lengths
    2.12 feet X 13 (100 foot lengths) =
    = 27.56 feet of total head loss
    Will this work? – Yes but not ideal – go bigger!

## Slide 94: Step 3 Cont.: Determine Pipe Diameter
    1. Use the Penstock chart to determine friction losses / 100 feet of pipe.
    2. Look-up your designed flow on
    the left column (100 GPM)
    3. Total loss of 4 inch pipe (on chart)
    = 0.25 psi or 0.578 feet
    5. Multiply by # of 100 foot lengths
    0.578 feet X 13 (100 foot lengths)
    = 7.51 feet of total head loss
    Will this work? Yes – just over 5% loss

## Slide 95: Step 4: Determine Friction losses in fittings
    Refer to friction loss tables for fittings, valves, and bends.
    Use the “Equivalaent length of feet” charts for easy calculations.
      Determine number of fittings of each type.
      Find the total equivalent length of feet of pipe
      Determine friction loss of for # of feet for each material.
      Add to total losses in head calculations.

## Slide 96: Step 5: Calculate Dynamic / Net Head
    Subtract the total loss of head for length of pipe based on the chart from the static head measurement.
    Our example:
      140 feet of total static head
      7.51 feet of total head loss (NOT including fittings)
      140 feet of static head – 7.51 feet of total loss =
      132.49 feet of Dynamic / Net Head!

## Slide 97: Step 6: Determine Nozzle Size
    Use the chart from the manufacturer to determine number and size of nozzles for the turbine.
    Step 1: Find Dynamic/Net head on the left column.
    Step 2: Find a combination of nozzles that will provide the amount of flow you have.
    Remember: For harris hydro systems, a 0.5 inch nozzel is the limit for a Pelton Wheel

## Slide 99
WOW, that is a weak chart! What happens between 120 and 150 feet of head?

## Slide 100: Step 6: Determine Nozzle Size (using linear interpolation)
    To make an accurate calculation use LINEAR INTERPOLATION
Linear Interpolation: Calculating a value based on known values both higher and lower.
How do we use it to determine NOZZLE FLOW?
Find the higher and lower known values for DYNAMIC HEAD and the known FLOW RATES for a certain NOZZLE SIZE.
Use the formula below:
High Head Value - Lower Head
High Head Nozzle Flow rate - Lower Head Nozzle Flow Rate
=
High Head Value - Your Cal. Head__
High Head Nozzle Flow Rate - X
Solve for: X

## Slide 101: Step 6: Determine Nozzle Size (using linear interpolation CONTINUED)
    EXAMLE PROBLEM:
High Head Value
High Flow
Rate
Low Head Value
Low Flow
Rate

## Slide 102: Step 6: Determine Nozzle Size (using linear interpolation CONTINUED)
    EXAMPLE PROBLEM:
150 - 120_______
46 - 41.2
=
150 - 132.49__
46 - X
30____
4.8
=
17.51__
46 - X
30____
4.8
=
17.51__
46 - X

## Slide 103: Step 6: Determine Nozzle Size (using linear interpolation CONTINUED)
    EXAMPLE PROBLEM:
30____
4.8
=
17.51__
46 - X
30(46 – X)
=
84.048
1380 – 30 X
=
84.048
1380 – 30 X
=
84.048
+30 X
+30 X
1380 = 30 X + 84.048
- 84.048
- 84.048
1295.95 = 30 X
30
30
X = 43.1 GPM

## Slide 104
Does it 43.1GPM Seem Right? YES, it looks good!

## Slide 105: Step 6: Determine Nozzle Size (using linear interpolation CONTINUED)
    To Determine Nozzle Size:
    Repeat the above steps for each nozzle size
    Find a nozzle combination that totals your overall calculated flow.
      Well, two 7/16 inch nozzles would give us 86.3 GPM (43.1 X 2 = 86.3)
        We need 100 GPM.
    What do we do?

## Slide 106
Refer to the chart and find another nozzle that will work
We need about 14 GPM flowing through a 3rd nozzle.

## Slide 107: Step 6: Determine Nozzle Size (using linear interpolation CONTINUED)
    After using the linear interpolation formula on the ¼ inch nozzle we get:
    14.006 GPM for 132.49 Feet of Head
    so
    86.3 GPM for two 7/16” nozzles + 14.006 GPM for one ¼” nozzle gives us a total of:
    100.306 GPM
    WILL THIS WORK?
    YES!!!!!

## Slide 108: Turbines

## Slide 109
http://www.waterwheelfactory.com/francis.htm
Francis
Reaction Turbines
Submerged in the flow;
driven by the pressure differential
http://www.youtube.com/watch?v=tjTh7A4jnbc

## Slide 110: Kaplan Turbine
Reaction Turbines
Submerged in the flow;
driven by the pressure differential

## Slide 111
Banki
Crossflow
Banki and Crossflow
Impulse – sheet of water

## Slide 112: Pelton Impulse – jet of water

## Slide 113: Turgo: More water than pelton

## Slide 115: LowPower Engineering aka Harris Hydro
20-600 feet of head
2-250 GPM of flow
1 nozzle $1850
2 nozzle $1950
4 nozzle $2200
707-986-7771
denisl@wildblue.net
http://harrishydro.biz/

## Slide 116: Energy Systems & Design
Stream Engine
Heads from 6 to 300 feet.
www.microhydropower.com
2 Nozzle Bronze $2395
4 Nozzle Bronze $2545
High Voltage Option $200
High Current Option $100

## Slide 117: Energy Systems & Design
Low Head Propeller Turbine
heads of 2 feet up to 10 feet.
At the maximum head, the output is 1 kW.
www.microhydropower.com
Water Baby
Operates much the same as the Stream Engine but requires very little water (pelton wheel)
Will operate on as little as 3 gpm but requires at least 100 feet of head.
Baby Generator, 1 Nozzle (12/24 volt) | 
Extra Nozzles (installed) | 
High Voltage (48/120 volt) | 
LH1000 with Draft Tube | 
High Voltage Option | 
High Current Option | 

## Slide 118: Hydro Induction Power
Good for long wire runs, 60' - 500' head, 10 - 600 gpm
The units produce 3-Phase 120V, 240V, or 480V 'wild' (unregulated) AC, which is then stepped down to battery voltage.
The heavy-duty brushless alternator is housed on the Harris Housing
www.hipowerhydro.com
HV 600 with 2 Nozzles $2500
HV 600 with 4 Nozzles $2600
HV 1200 with 4 Nozzles $3000
HV 1800 with 4 Nozzles $3500
HV 3600 with 4 Nozzles $5000
Turgo option $600

## Slide 119: Hydro Induction Power
Now offer a new LOW VOLTAGE (12V/24V), brushless unit (48V coming in 2006).
It can generate either 12V or 24V with pressures from 20psi to 150psi (46' - 400'). Above this pressure, it will generate 48V.
12/24V Hydro with 1 Nozzle: $1350
12/24V Hydro with 2 Nozzles:$1400
12/24V Hydro with 3 Nozzles:$1450
12/24V Hydro with 4 Nozzles:$1500
Upgrade from Harris Hydro: $500
Turgo option $600
www.homehydro.com

## Slide 120: Power Spout
http://www.powerspout.com/

## Slide 121: Canyon Hydro
Serious engineering
185
4084
101
3335
36
2415
12
1665
KW
gpm
Canyon 2435
15
340
8
277
3
197
1
139
KW
gpm
Canyon 751
300
200
100
50
100 KW Canyon Crossflow
www.canyonhydro.com
Great
Resource

## Slide 122: Alternative Power & Machine
Economy models
Permanent magnet units
Accessories
Niche: Ease of maintenance and adjustment
www.apmhydro.com

## Slide 123: Other
www.ampair.com....it’s a wind and hydro turbine
$1300
The Jack Rabbit, just drop it into the river
$1295

## Slide 124: Electricity and Microhydro Balance of System

## Slide 125: First Things First. What does a microhydro turbine produce?
Wild Alternating Current (Wild AC) most of the time
  “Wild” due to the fluctuating voltage, current and frequency.
  Why is this?
    Most modern small hydro turbines are direct drive permanent magnet systems (there are exceptions)
  In most cases the wild AC needs to be rectified.
    Conversion of Alternating Current (AC) to Direct Current (DC)
WILD AC
DC
120 AC @ 60Hz

## Slide 126: Electricity from a Spinning Shaft
http://www.reuk.co.uk/OtherImages/moving-magnet-past-wire-to-make-current.jpg
Click Here for Animation

## Slide 127: Why Alternating Current?
Simplicity of permanent magnets alternators
This AC power is rectified to Direct Current regardless of battery or grid-tie configuration.
3 phase output is most common
http://bp1.blogger.com/_Ist6QgbdKFo/SIsThFlYcTI/AAAAAAAAAGw/-cBy0MQjDvI/s400/5.bmp

## Slide 128: Why Three Phase?
Most effective use of space and materials!

## Slide 129: What is the BOS?
DC only system (small cabin)
  Charge controller
  Batteries
Conventional AC system (house)
  Charge controller
  Batteries
  Inverter

## Slide 130: Typical Off-Grid Battery Charging System

## Slide 131: Off-Grid Batteryless System

## Slide 132: Grid-Tie Batteryless System

## Slide 133: Electrical Transmission / Wire Run

## Slide 134: Wire Run / Wire Sizing
Needed information:
  Distance from turbine to load
  Voltage of the turbine
  Max output of the turbine
  Type of output? AC or DC, 3 phase or single phase.
Important Considerations
  Diameter of wire (American Wire Gauge – AWG)
  Length of wire
  Free Air or Conduit
  Type of insulation on wire
  Temperature of location where wire located
  Moisture where wire is located
  Will conductor be exposed to sunlight
  Color of insulation
  Voltage Drop

## Slide 135: Good location of turbine to load
Turbine Powerhouse

## Slide 136
2,000 foot wire run

## Slide 137: Ampacity
The quantity of electrons or amperes that a conductor can safely carry
  Factors affecting ampacity
    Size (diameter) of wire
    Type of wire (copper or aluminum)
    Insulation
    Temperature

## Slide 138: American Wire Gauge (AWG)

## Slide 139: Wire Sizing for DC Applications
Voltage drop is caused by a conductors electrical resistance
This voltage drop can be used to calculate power loss
For DC systems – efficiency is paramount!
Voltage Drop (Volts) =
Electrical Resistance (Ohms) X Current (Amps)
Power Loss (Watts) = Ohms X Amps²
Power Loss (Watts) =
Voltage Drop (volts) X Current (Amps)

## Slide 140: Voltage Drop
Voltage drop occurs when too many amps try to pass through a conductor which is too small
If volts are lost then power is lost!
Power Loss = Voltage Drop x Amps
Need to assess Voltage Drop to avoid wasting power and compromising system performance
Vdrop = I (current) x R (resistance)
Typically will require a larger wire than required for ampacity rating
NEC REQUIREMENT: Article 215.2 requires no more than 3% drop for feeder ciricuits, and 5% drop for feeder and branch circuits combined.

## Slide 141: Calculating Voltage Drop
According to NEC
  For 2-wire DC circuits, 2-wire AC circuits
  VD = 2 X L X R X I
  1000
  VD = Voltage drop @ 75 degrees C
  L = one-way length of circuit (ft)
  R = conductor resistance in ohms / 1000 feet
  I = load current (amps) – assumed as supply current as well.

## Slide 142: Voltage Drop Calculation
VD = ?
L = 500 feet
AWG = 00
R = ?
I = 20.8
For resistance of conductor see chapter 9 TABLE 8 in NEC Handbook.
  VD = 2 X 500 X 0.101 X 20.8
  1000
  VD = 2.10 volts

## Slide 143: VDI Voltage drop Index
Easy method for determining wire size
What you need to know
  Amps (Watts/volts)
  Feet (one-way distance)
  Acceptable % volt drop
  Voltage

## Slide 144: How to Use Formula and Chart
Example: 1 KW, 24 volt system, 50 feet, 3% drop
Amps = 1000 watts/ 24 volts = 41.67 amps
VDI = 41.67 amps * 50 feet = 28.9
3% * 24 volts

## Slide 145: VDI Chart
24V VDI = 28.9
2 AWG wire
That’s pretty big wire
What if we make it a
48 volt system?

## Slide 146: How to Use Formula and Chart
Example: 1 KW, 48 volt system, 50 feet, 3% drop
Amps = 1000 watts/ 48 volts = 20.8 amps
VDI = 20.8 amps * 50 feet = 7.23
3% * 48 volts

## Slide 147: VDI Chart
48V VDI = 7.2
8 AWG wire
That’s better
(smaller, less $,
same losses).

## Slide 148: How to Use Formula and Chart
Example: 1 KW, 160 volt system, 50 feet, 3% drop + Midnite classic
Amps = 1000 watts/ 160 volts = 6.25 amps
VDI = 6.25 amps * 50 feet = 0.65
3% * 160 volts

## Slide 149: VDI Chart
160V VDI = 0.65
16 AWG wire
That’s so much better
(even smaller, much
less $, same losses).

## Slide 150: Charge Controllers

## Slide 151
Basic Functions
  To prevent overcharging a battery, which could damage it and shorten its life and possibly some loads powered by it
Purpose of Charge Controller

## Slide 152: Features to Consider
Voltage Rating
Charge control algorithm
Amperage rating (plan for future expansion)
Source of Electricity (PV, Wind, Hydro)
Adjustability
Temperature Compensation
Meters
Low battery voltage disconnect or alarm
Wire terminals

## Slide 153: Conventional Charge Controllers
For Solar System

## Slide 154: Typical (traditional) Charge Controllers For Wind and Hydro

## Slide 155
Basic Types of Charge Controllers
Interrupting –Type Switches charging current off and on.
  Least expensive and simplest type
  Best for flooded batteries
Linear-Type or Pulse Width Modulating (PWM)
  Limits charging in a gradual manner
  Compatible with more types of batteries

## Slide 156
Multiple Stage Charging
(for most RE batteries)
Stage One (Bulk Mode)
  A preset maximum constant amount of current (amps) is put into the battery. As this occurs, the voltage increases
Stage Two (Absorption Mode)
  After a preset voltage is reached (14.2 volts for a 12 volt systems) the voltage is then held constant. As the battery continues to charge at constant voltage, the current decreases.
Stage Three (Float Mode)
  When the current has decreased to a preset low limit, or a set amount of time has passed (absorption time), then the controller switches to Float Mode. Now the battery is kept at a preset Float voltage, and a small amount of power (amps) is supplied, as required to maintain the preset voltage.

## Slide 157: Battery Charging
Home Power May 2012

## Slide 158: Pulse Width Modulation Charge Controllers
The third stage requires current to slowly decrease and voltage to remain the same
PWM Achieves this by rapidly switching current on and off
By adjusting the width of the pulses (pulse width modulation) the current that the battery "sees" can be adjusted.
Thus, the controller is able to provide a fine control.

## Slide 159: Maximum Power Point Tracking Controllers (MPPT)

## Slide 160: MPPT Controllers
Can significantly increase 30% more power
Looks at the output current, and compares it to the battery voltage
Determines the best power that the system can provide to charge the battery. Then, converts the “power” to the best voltage to get maximum AMPS into the battery.
Most modern MPPT's are around 92-97% efficient in the conversion.
You typically get a 20 to 45% power gain in winter and 10-15% in summer. (for solar systems)

## Slide 161: A class of its own!!!
http://www.midnitesolar.com/video/classRunOver/classicRunOver.php

## Slide 162: The Midnite Solar Classic
“A revolution in charge controller technology”
  Michael Uchal
http://www.midnitesolar.com/ (Home site)
http://www.midnitesolar.com/products.php?menuItem=products&productCat_ID=21&productCatName=Charge%20Controllers%20-%20Classics (Classic)
http://www.midnitesolar.com/videoDisplay.php
(Educational Videos)

## Slide 163: What if one charge controllers is not enough?
Answer: Parallel configuration

## Slide 164: Diversion Loads AKA “Dump Loads”

## Slide 165: Why a Diversion Load?
Protect the turbine!
  “Most” small scale hydro turbines can not run unloaded.
Protect the battery bank from overcharging.

## Slide 167: Basic Diversion Loads
Air Heating
Water Heating

## Slide 168: Dump Loads and the National Electric Code
1: Dump Load MUST be able to safely handle 1.5 times the total power output of the turbine.
2: Must be installed in a manner that isolates it from flammable materials.
3: The amperage rating of the controller must be at least 30% higher than the dump load current.

## Slide 169: Batteries in Renewable Energy Systems

## Slide 170: Presentation Outline
Why batteries?
Battery basics
Battery operation
Terminology
Battery charging/discharging
Battery sizing
Battery maintenance
Batteries and the National Electric Code

## Slide 171: Why are batteries needed?
  For off-grid, and battery back-up renewable energy systems. batteries are needed to:
    Store energy provided from the charging systems for later use to power loads.
    Provide enough power for any power surges that occur within the electrical system.
    Batteries in some small grid-tied RE systems are used for power conditioning purposes for the grid interconnection.

## Slide 172: Battery Types
Batteries can be classified by:
  Non-rechargeable (primary) (disposable)
  Rechargeable (secondary)
  Application
    Automotive, electronics, deep-cycle (renewable energy), marine applications
  Construction
    Chemistry
    Flooded
    Gelled
    Absorbed Glass Mat (AGM)

## Slide 173: Deep-Cycle Lead-Acid Batteries

## Slide 174: Deep Cycle vs. Other Tech.
Deep Cycle
Lower in cost
Rechargeable
Deliver energy over a long period of time.
Recyclable
Long life if maintained
Slower discharge rate.
Other Battery Types
Alkaline – non-rechargeable
Lithium-ion
Nickel-metal hydride
  Both in cordless tools
Nickel-cadmium
The list goes on!
Uses: Tools, electronics, electric cars, etc.

## Slide 175: Components of a Lead Acid Battery
Anode plates (Lead Dioxide when charged, lead sulfate when discharged), positive
Cathode Plates (Lead when charged, lead sulfate when discharged), negative
Electrolyte 35% sulfuric acid and 65% water solution when charged; water when discharged.

## Slide 176: Principle of Operation
The cell has one plate made of lead (cathode or negative) and another plate made of lead dioxide (anode or positive), with a strong sulfuric acid electrolyte in which the plates are immersed.
Lead in cathode combines with SO4 (sulfate) to create PbSO4 (lead sulfate), plus electrons.
Lead dioxide, hydrogen ions and SO4 ions, plus electrons from the lead plate, create PbSO4 and water on the lead dioxide anode plate.
As the battery discharges, both plates build up PbSO4 and water builds up in the acid. The characteristic voltage is about 2 volts per cell, so by combining six cells you get a 12-volt battery.
The reaction is completely reversible. If you apply current to the battery at the right voltage, lead and lead dioxide form again on the plates so you can reuse the battery over and over. In a zinc-carbon battery, there is no easy way to reverse the reaction because there is no easy way to get hydrogen gas back into the electrolyte.

## Slide 178: Flooded Lead-Acid Battery info:
For most Renewable Energy Systems the following battery info must me known:
  Battery Capacity
  Battery Nominal Voltage
  Number of cells
  Specific charging / discharging information
  Temperature compensations

## Slide 179: Battery Capacity (Amp-Hours)
Battery capacity is rated in amp-hours.
  1 amp-hour is the equivalent of drawing 1 amp steadily for one hour, or 2 amps steadily for half an hour.

## Slide 180: Formula for Amp-Hours
To determine the amp-hours used:
Amps (used by load) X Time =
Amps-hours used

## Slide 181: Battery Capacity (Amp-Hours)
Question:
If you were to use a load that requires 30 amps for 25 minutes. How many amp hours have you used?
Answer:
30 amps X (25min / 60min in 1 hour) =
30 amps X 0.41 hours =
12.5 Amp-Hours

## Slide 182: Factors Affecting Battery Capacity
Rate of discharge
Depth of discharge
Temperature
Age
Recharging characteristics

## Slide 183: Series and parallel connections
Battery banks are designed, not just purchased.
  A RE battery bank can be designed to fit the needs of the system.
    Series connections: Voltage increases, amperages stays the same.
    Parallel connections: Amperage increases, voltage stays the same.

## Slide 184: Series Connections

## Slide 185: Parallel Connections

## Slide 186: Series & Parallel

## Slide 187: 12 Volt Batteries

## Slide 188: 24 Volt Batteries

## Slide 189: 48 Volt Batteries

## Slide 190: Energy in Batteries:
Battery capacity can also be expressed in Power
  If Watts is equal to Amps X Volts
  Then Watt-hours is equal to Amp-hours X Volts
    This concept will help with battery sizing later.

## Slide 191: Battery Charging
Lead-Acid batteries in RE systems utilize 3 stages of charging:
  Bulk – Stage 1: high amperage increasing voltage
  Absorption - Stage 2: Decreasing amperage, steady voltage
  Float - Stage 3: lower amperage, steady but lower voltage

## Slide 192: Battery Charging
Home Power May 2012

## Slide 193: What is the C-Rate?
The rate of charge/discharge of the battery.
Often expressed in C/5, C/10, C/20, etc.
  The “C” is the total battery capacity
  The #/rate is the amount of hours for charge/discharge
EXAMPLE:
C-rate of C/10 for a 350 amp-hour battery would be:
  350 amp-hours / 10 = 35 amps for 10 hours

## Slide 194: C-Rate continued:
Another EXAMPLE:
If you have a completely discharged battery bank with a total capacity of 440 amp-hours and you wish to charge it at a C-Rate of C/20, how many amps are needed for how many hours to fully charge this battery bank?
Answer: 440 amp-hours / 20 hours=
22 amps for 20 hours
NOTE: This is a very simplified example. This calcuation does not take in account temperature and different charging algorithms.

## Slide 195: C-Rate and RE batteries
In most cases, C/20 is suggested for deep cycle, flooded, lead acid battery charging in RE systems. And no faster than C/10 for discharging (typically).
What up with that?:
  Higher currents during charging provided to the battery at faster C-Rates (C/10, C/5) produce excessive heat that can structurally damage the plates of the batteries. Heat also increases electrical resistance which wastes energy. For these reasons, a slower C-Rate such as C/20 is suggested for longer battery life, less wasted energy resulting in less system maintenance cost.

## Slide 196: C-Rate and Battery Performance

## Slide 197: State of Charge (SOC)
SOC refers to how charged, or discharged a battery is given in a percentage.
The SOC can be determined by:
  Voltage (low accuracy)
  Specific Gravity of the electrolyte (Most Accurate)
  Amp-hour meters (specific equipment - accurate)

## Slide 201: Hydrometer Readings

## Slide 202: Hydrometer Readings

## Slide 203: Amp Hour Meters

## Slide 204: Preventative Battery Maintenance
Prevent damage to your batteries by:
  Regular Equalization Charges
  Keeping electrolyte levels correct
  Keep your batteries warm
  Keep your batteries charged.

## Slide 205: Equalization Charge
Over several cycles of the batteries charging/discharging, the separate cells that make up the nominal battery voltage will not all be equal to 2 VDC (nominal). If the difference in voltage from cell to cell is greater than 0.05 VDC, an equalization charge is needed.

## Slide 206: What is an equalization charge?
A controlled “overcharge” of a currently full battery bank.
Often performed at the C/20 rate for a period of several hours (possibly 6 – 7 hours)
  Many solar, wind, and hydro charge controllers can perform equalization charges manually or programmed to do so every 1 – 3 months.
  Sometimes a generator is needed for off-grid systems to provide consistent energy during this time.
  Often needed 4 – 12 times a year depending on battery charge/discharge cycles.

## Slide 208: Removing Sulfation
Charge at 2.6 to 2.7 - volts per cell (equalization charge)
Low current rate (approximately 5 Amps for small batteries and 10-Amps for larger ones) until the specific gravity of the electrolyte starts to rise.
Be careful not to let the internal temperature of the battery rise above 125° F. If it does, turn the charger off and let the battery cool.
Continue charging until each cell in the battery is brought up to full charge (nominal 1.265 specific gravity or higher).

## Slide 210: Hydro Caps

## Slide 211: Water Miser Caps

## Slide 212: Battery Maintenance
Cleaned using a baking soda and water mix; a couple of table spoons to a pint of water. NEVER CLEAN WITH CAPS OFF.
  Be very carful to not allow ANY of this solution into the battery cells!!!
Cable connection needs to be clean and tightened.
Check fluid level. Use Distilled water. Only fill a charged battery, never a fully discharged battery.
To prevent corrosion of cables on top post batteries use a small bead of silicon sealer at the base of the post and place a felt battery washer over it. Coat the washer with high temperature grease or petroleum jelly (Vaseline), then place cable on the post and tighten. Coat the exposed cable end with the grease.

## Slide 213: Battery Bank Sizing
Needed Information:
  Total amp-hours needed by the load per day.
  Total surge capacity (in amps) that will be required of the system
  System voltage
  Battery temperatures
  Total number of storage days
  Lowest battery SOC desired

## Slide 214: Step 1: Amp-hours
Determine the total amp-hours that needs to be supplied to the load per day.
  For example: Lets assume a home uses a conservative 6,000 kWh/year and a potential for 700 watts of 48 volt hydro output.
    How many amp-hours per day does the house use?
    Answer: 6,000 kWh X 1000 watts in 1 kW =
              6,000,000 watt-hours per year =
              6,000,000 / 365 days per year =
              16,438 watt-hours per day =
              16,438 watt-hours / system voltage (48vdc) =
              343 amp-hours per day (estimated)

## Slide 215: Step 2: Account for inverter losses?
Since we are storing energy in DC batteries that will be used for AC loads, an inverter(s) will be used. Inverters lose energy in the inversion process.
Account for this by dividing your daily amp-hour use by 0.90 (90% inverter efficiency).
  NOTE: Check the efficiency of your specific inverter
343 amp-hours / 0.90 =
381.11 (rounded to 380 amp-hours per day)

## Slide 216: Step 3: Number of storage days
Next, multiply the amp-hours needed per day by the number of days you wish to go without your RE resource.
Hint: for hydro alone, it is easy. Assume 1 day since this resource is continuous. for wind, it is difficult – when will the wind blow?
                Great questions!
For solar – think 3-5 days.
If your hydro resource can cover your energy use multiply your amp-hours per day by 1
  380 X 1 = 380 amp-hours per day

## Slide 217: Step 4: Battery Reserve
Deep-cycle batteries need to maintain a reserve on their charge. 20% is the least, 50% is much better. 80% - BOOYAH!!!!
  Lets assume 50% reserve on this system.
  Account for the 50% reserve by dividing your amp-hours per day by 0.5
    380 amp-hours per day / 0.5 = 760 amp-hours

## Slide 218: Step 5: Account for temperature of battery bank:
Based on the temperatures your batteries will operate in, the capacity of your bank could be compromised.
For lower temperatures, the bank must be sized larger to account for low efficiencies.

## Slide 219: Account for Temperature of battery bank:
Lets assume your batteries could experience conditions around 50 degrees.
Multiply your capacity (760 amp-hours) by the given correction factor (manufacturer dependent)
760 amp-hours X 1.19 (temp. correction factor) = 904 amp-hours
Suggestion: store your batteries in a climate controlled space and reduce the size of your batteries. It’s a balancing game of cost.

## Slide 220: Step 6: Heavy Electrical Loads
Determine if any heavy surges will be needed to be supplied by this system. If so, what are they?
Let assume that at any given time, this system will need to provide a total of 4.5kW to 120 volt loads at one time for just a few moments. What is this in DC amps?
  4500 watts = Amps X Volts
  4500 watts / 48 volts =93.75 amps.

## Slide 221: Heavy Electrical Loads Continued:
93.75 amps of potential DC surge.
Consider that we have a total of 700 watts of continuous power provided from the hydro turbine.
  How many amps is this?
    Watts = amps X volts
    700 watts / 48 volts = 14.5 amps
    So how many amp must the battery supply to make up for what the hydro cant?
    93.75 amps needed minus (-) 14.5 amps from hydro =
              79.25 amps from the battery WOW, that’s a lot.

## Slide 222: Heavy Electrical Loads Continued:
Can the battery safely supply 79.25 amps?
  Consider your C-Rate
  C/20 =
    total battery capacity / 20 hours (for a C/20)
    904 amp-hours / 20 hours = 45.2 amps
  C/10=
    Total battery capacity / 10 hours (for C/10
    904 amp-hours / 10 hours = 90.4 amps
  What the C-rate for 79.25 amps?
    904 amps / Hours = 79.25 amps
    904 amp-hours / 79.25 amps = 11.4 hours
    So this C-Rate = C/11.4
    Yes, this battery bank can handle it without any problems

## Slide 223: Step 7: Battery Bank Size
Your designed battery bank of 904 amp-hours:
  Can provide all energy used by residence.
  Can run those loads for 1 full day without hydro input.
  Only will drop to 50% SOC after one day
  Has been sized for 50ºF
  Can easily handle any surge of the residence.
WOW, that’s a big battery.

## Slide 224: Step 8: Choose the batteries
OK you need a 48 VDC 904 amp-hour battery
  Can you purchase such a battery? NO
  So what do you do? BUILD ONE!
  Choose several 6 or 12 VDC batteries from a manufacturer to make the battery you need.

## Slide 225: Step 8: Choose the batteries
Lets assume you find Trojan T-105-RE
  Voltage: 6 VDC
  Capacity: 225 amp –hours
Now what? You need 904 amp-hours
Divide total amp-hours needed by
the individual amp-hours of the
battery.
904 / 225 = 4.01 (rounded down to 4)
  This is the number of parallel strings you need.

## Slide 226: Step 8: Choose the batteries
You need 4 parallel strings to achieve the capacity.
  Be care carful with 4 parallel strings – Most charge controllers can not charge over 2 strings equally!!!!!
What about voltage?
Voltage of system / voltage of each battery
  48 vdc / 6 vdc = 8 batteries in series.
  Total # of batteries = Total parallel strings X number of batteries in series
  4 parallel strings X 8 batteries in series = 32 batteries

## Slide 227: COST
How much will this battery bank cost?
Each T-105RE costs as high as $225 each
32 batteries X $220 a pop
WOW, that $7,040 just for batteries.
What can you do to improve this system?

## Slide 228: Suggestions to reduce the battery bank size:
Consider the power input from the RE system. Remove this power from your total energy needed for the residence!
Choose a 20% SOC of your battery bank after 1 day of full use.
Climate control your battery bank!!!!!!!
Commit to conservation of energy use

## Slide 229: Batteries and the National Electric Code
Article 480: Storage Batteries
  Mostly information for industrial / commercial systems of higher voltages above 50 VDC nominal
  For all storage batteries
    480.9 (A) ventilation.
      Provisions shall be made for sufficient diffusion and ventilation of the gases from the battery to prevent the accumulation of an explosive mixture.

## Slide 230: Batteries and the National Electric Code
Special Equipment
  The NEC provides code requirements for wind and solar systems, but not hydro.
  It is safe to assume that the same requirements apply to Hydro
Article 694 Small Wind Electric System
  VIII. Storage batteries
    6940.70(B)(1) Operating Voltage
      Storage batteries shall have the cells connected to operate at less than 50 volts nominal. Lead-acid storage batteries shall have no more than twenty-four 2-volt cells connected in series (48 volts, nominal)

## Slide 231: Batteries and the National Electric Code
Article 694 Small Wind Electric System
  VIII. Storage batteries
    694.70(B)(2) Guarding of Live Parts
      Live parts of battery systems shall be guarded to prevent accidental contact by persons or objects, regardless of voltage or battery type.
  694.70(C) Current Limiting.
    A listed, current-limiting overcurrent device shall be installed in each adjacent circuit adjacent to the batteries when the available short-circuit current from a battery or battery bank exceeds the interrupting or withstand rating of other equipment in that circuit. The installation of current-limiting fuses shall comply with 694.26

## Slide 232: Batteries and the National Electric Code
Article 694 Small Wind Electric System
  Basically,
    Keep your batteries at 48 volts or less nominal
    Vent the battery bank
    Enclose the battery bank
    Fuse your connections

## Slide 233: Inverter Technology

## Slide 234: Inverters:
Invert Direct Current (DC) to Alternating Current (AC)
Step up voltage to useable amounts (120,240)
12 Volts DC battery
120 Volts AC

## Slide 235
INVERTER
DIRECT CURRENT
ALTERNATING CURRENT
INVERTER

## Slide 236: Inverter Basics
Power rating
  Amount of power (watts) an inverter can provide to the loads.
    Continuous Power Rating: Amount of power (watts) an inverter can continually provide to the loads
    Surge Power Rating: Amount of power (watts) an inverter can provide to loads for SHORT periods of time.
Input Voltage
  Input voltage the inverter is designed to accept.
    Battery based inverters accept nominal voltages of 12,24, and 48 volts DC

## Slide 237: Inverter Basics
Input Voltage Continued
  Grid-Tied inverters often accept 200 – 600 VDC
    Most Hydro electric grid-tied inverters are specified by the wind turbine manufacturer.
Idle Power Consumption
  Amount of power the inverter uses when not in OPERATION
Inverter Options
  Low Voltage Disconnect: Inverter shuts off at low input voltage.
  Generator input: inverter has internal battery charger or ability to run AC loads directly from motorized generators for low wind/solar input.

## Slide 238: Inverter Technology
NOT ALL INVERTERS ARE CREATED EQUAL
Inverter Types:
Battery (off-grid) inverters
Grid-Tie with battery backup
Batteryless grid-tied

## Slide 239
NOT ALL INVERTERS ARE CREATED EQUAL
Inverter AC Outputs
Square Wave
Modified Square Wave
Stepped Sine Wave
Pure Sine Wave
http://www.dansdata.com/images/diyups/waveforms600.jpg

## Slide 240: Square Wave Inverters
Low cost, Low Performance
Alternates b/w 120 volts + and 120 volts –
Subjects electronics to voltage fluctuations based on battery voltages
Home Power 134

## Slide 241: Modified Square Wave Inverters
Much like the square wave tech. but with an added OFF function between + and – pulses.
Still low performance but better than Square wave.
Most common low cost battery based inverters
Not suitable for grid-tie applications
Often marketed as “Modified Sine Wave” inverters
Home Power 134

## Slide 242: Stepped Sine Wave Inverters
Improvement over the modified square wave with MORE “steps”
Efficiencies up to >90%
Often NOT grid-tied but suitable for off-grid battery based applications.
Higher in price with higher performance.
exeltech
Home Power 134

## Slide 243: PURE/TRUE Sine Wave Inverters
A TRUE sine wave that matches GRID power (Sometimes BETTER)
Efficiencies greater than 95%
Off-Grid and Grid-Tied applications
Higher cost but BEST performances
Meets UL 1741 (Distributed Energy Resources) Certification
Digital and microprocessor controlled
Home Power 134

## Slide 244: Battery Based Off-Grid Inverters
Make usable AC power from input DC battery voltage where grid connection is not an option or desired.
INVERTER

## Slide 245: Battery Based Off-Grid Inverters
Requirements:
Inverter input voltages
  12,24, or 48 volt nominal voltages
Inverter output:
  Total output for stand-alone systems must be sized to supply the load of the largest single piece of utilization equipment (NEC 694.18)
  Inverters should be sized to meet the total load requirements of any possible surges.
Utility interactive equipment NOT needed.

## Slide 246: Off-Grid Battery Based Inverters
Outback FX & VFX
Magnum MS
Sunny Island

## Slide 247: Grid-Tie with Battery Backup

## Slide 248: Grid-Tie with Battery Backup
Requirements:
  Input Voltage: Nominal battery voltage (12,24,48)
  Grid-interactive: Only inverters listed and identified as interactive shall be permitted in interactive systems (NEC 694.60)
  Inverter Output: same rules apply for off-grid system power output.
    (UL 1741)
    120 / 240 VAC @ 60Hz

## Slide 249: Grid-Tie with Battery Backup
OutBack G-Series
The Sunny Island 5048-US
Xantrex XW

## Slide 250: Batteryless Grid–Tied Inverters

## Slide 251: Batteryless Grid–Tied Inverters
Requirements:
  Input voltage: Must accept voltage range of turbine.
  Inverter Output: Must be able to output total hydro turbine rated output.
    120 / 240 VAC @ 60Hz
  Grid Interactive: (NEC 694.60) (UL 1741) (Distributed Energy Resources)

## Slide 252
Sample Last Slide
This concludes The American Institute of Architects Continuing Education Systems Course
Contact Information:
energy.appstate.edu Janet Miller, millerjm1@appstate.edu
Follow us on Facebook!
AppEnergyCenter